TOTUS Modbus Python Integration Application Note

Author: David Luca

Table of Contents

[Document History 1](#_Toc399744908)

[Introduction 2](#_Toc399744909)

[Configure MODBUS on TOTUS 2](#_Toc399744910)

[1. Configure Modbus via TCP 2](#_Toc399744911)

[2. Configure Modbus via Serial 3](#_Toc399744912)

[Totus Modbus Register map 3](#_Toc399744913)

[Pre-requisites 4](#_Toc399744914)

[Jamod setup 4](#_Toc399744915)

[Project Setup 6](#_Toc399744916)

[1 Connecting to Totus 7](#_Toc399744917)

[1.1 Connecting via TCP 7](#_Toc399744918)

[1.2 Connecting via Serial 8](#_Toc399744919)

[2. Reading values from Totus unit 8](#_Toc399744920)

[2.1 Reading temperatures 8](#_Toc399744921)

[2.2 Reading alarms 9](#_Toc399744922)

[2.3 Reading DGA values 9](#_Toc399744923)

[Conclusions 10](#_Toc399744924)

# Document History

|  |  |  |  |
| --- | --- | --- | --- |
| Revision | Date | Author | Comments |
| 0.1 | 29/09/2014 | David Luca | First draft |

# Introduction

The purpose of the document is to introduce customers into using available MODBUS software libraries to connect their software to TOTUS instruments.

This document assumes you can access Totus interface by typing in your browser the IP address of the unit (in this document we will use <Totus-IP>). You may have to setup VPN connection, for which you need to contact Camlin Technologies.

# Configure MODBUS on TOTUS

## Configure Modbus via TCP

On TOTUS web interface navigate to **Settings**->**MODBUS** page. Press “Add New MODBUS Interface”, select “New TCP interface” then type in the form SlaveID (default 1) and the port to be used (i.e. 502, 1502) then press **Submit** button.



## Configure Modbus via Serial

On TOTUS web interface navigate to **Settings**->**MODBUS** page. Press “Add New MODBUS Interface” and select the Serial0, Serial1 or Serial2, specify on the form Baudrate, SlaveID (usually 1), data and stop bits, parity control, MODBUS protocol (ASCII/RTU) and flow control (usually “none” for RS232 or “hardware” for RS485 to enable direction via RTS line). For this application note we’ll be using 115200bps, 8 data bits, no parity, 1 stop bit then press **Submit** button.



# Totus Modbus Register map

On TOTUS web interface navigate to **Settings**->**MODBUS** page. Click on the link “Download Register Map” for this device to download the MODBUS map for this device. This is a table of MODBUS protocol description, meaning of the fields and register transfer requirements to read and/or write into the dictionary.

e.g.:

0000\_Common

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Topic** | **Address** | **Register** | **Number of Registers** | **Access** | **Format** | **Scaling** | **Offset** | **Notes** |
| UTC Time | 0 | 30001 | 2 | Read only | UINT32 |  |  | Clock time in UNIX time format; number of seconds from 1 Jan 1970. |
| ALARM/System/HL/State | 100 | 10101 | 1 | Read only | BOOLEAN |  |  | Combined system alarm for any non severe (H or L) alarm. |
| ALARM/System/HHLL/State | 101 | 10102 | 1 | Read only | BOOLEAN |  |  | Combined system alarm for any severe (HH or LL) alarm. |

# Pre-requisites

The code examples provided have been built using LiClipse IDE and Python 2.7 platform using latest version of Pymodbus from <https://code.google.com/p/pymodbus/>.

Dependencies needed: Setuptools (<https://pypi.python.org/packages/source/s/setuptools/setuptools-6.0.1.zip#md5=f35cd3a424145c68c235dcb7aef89c48>) then extract into an empty folder, open a command prompt into that folder and type: python setup.py install

For serial communications Pyserial library: <https://pypi.python.org/pypi/pyserial> ([pyserial-2.7.win32.exe](https://pypi.python.org/packages/any/p/pyserial/pyserial-2.7.win32.exe#md5=21555387937eeb79126cde25abee4b35))

If building under Windows install the compiler and set of system headers necessary for producing binary wheels for Python 2.7 packages from <http://aka.ms/vcpython27>

Download <https://code.google.com/p/pymodbus/downloads/detail?name=pymodbus-0.9.0.zip> and extract it into an empty folder then open a command prompt into that folder and type:

python setup.py install

Alternatively use SVN to checkout latest version of the library:

svn checkout http://pymodbus.googlecode.com/svn/trunk/ pymodbus-read-only  
cd pymodbus-read-only  
python setup.py install

Or from GitHub:


git clone <https://github.com/bashwork/pymodbus.git>

cd pymodbus


python setup.py install

# Project Setup

Create a new project using File->New->Project then select General->Project in wizard window, press **Next** button, type the project name (e.g. totus\_pymod) and select a folder then press **Finish**.



LiClipse will ask to configure an interpreter so “Manual config” can be selected to specify the path to Python environment, this can also be later configured from Window->Preferences menu, select PyDev->Interpreters->Python Interpreters in the left tree:



## 1 Connecting to Totus

Jump to section 1.1 if connecting via TCP or section 1.2 if connecting via Serial connection.

### 1.1 Connecting via TCP

The following example shows how to initiate a connection to Totus unit via TCP port specified in the settings form (502).

Imports required:

### 1.2 Connecting via Serial

Imports required:

## 2. Reading values from Totus unit

### 

### 2.1 Reading temperatures

### 2.2 Reading alarms

### 2.3 Reading DGA values

The floating point value are read as 16bit big endian values and assembled in a float using Convert2Float utility function:

# Conclusions

This document exemplified Modbus interfacing using Open-Source libraries for various programming platforms which allows customers to implement their own Human Machine Interface to extract information from Totus units.

Example output (values with 3276.7 are for not connected sensors):

****